## SelectionData
Selection Table SLS / SLB / SLF
flow rate, Q | [m³/h] | 400
diffuser length, L | [mm] | 1000
throw, LT | [m] | 4
supply temperature, Ts | [°C] | 18
room temperature, Tr | [°C] | 26
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-1 SLB-1 | SLS-2 SLB-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4
| L [mm] | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
Airflow direction
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
| Plenum | SP--1 | SP--2 | SP--3 | SP--4 | SP--1 | SP--2 | SP--3 | SP--4
effective air velocity, Veff | [m/s] | 7.2943 | 4.5268 | 3.2817 | 2.5738 | 6.2355 | 4.9336 | 4.0815 | 3.4804
static pressure, DPs | [Pa] | 101.8656 | 20.5025 | 11.0988 | 6.4018 | 36.469 | 14.1305 | 7.5996 | 4.7892
total pressure, DPtot | [Pa] | 151.0521 | 38.8259 | 18.6041 | 13.9071 | 85.6556 | 32.4539 | 15.1049 | 12.2944
throw velocity, vT @ LT | [m/s] | 0.56453 | 0.48291 | 0.44479 | 0.42472 | 0.48347 | 0.41602 | 0.36233 | 0.31538
critical distance | [m] | 18.4435 | 8.6774 | 5.5827 | 4.0826 | - | - | - | -
air temperature @ LT | [°C] | 25.7373 | 25.563 | 25.3635 | 25.1416 | - | - | - | -
sound power, Lw | [dB(A)] | >55 | 43.9087 | 37.9192 | 31.8842 | >55 | 39.9423 | 27.3697 | 24.0876
sound pressure, Lp | [dB(A)] | >55 | 35.9087 | 29.9192 | 23.8842 | 49.1208 | 31.9423 | <20 | <20
Sound Spectrum
|  | Lw [dB] |  |  |  | Lw [dB]
125 | [Hz] | - | 48.8821 | 47.2089 | 41.0797 | 43.5903 | 34.133 | 26.4002 | 24.6525
250 | [Hz] | - | 48.1077 | 42.8984 | 37.6162 | 49.1817 | 38.6469 | 30.0582 | 28.0799
500 | [Hz] | - | 42.1087 | 33.8657 | 27.0549 | 51.4441 | 36.5991 | 25.1177 | 21.7172
1000 | [Hz] | - | 37.8174 | 28.9024 | 20.7685 | 54.4391 | 36.3529 | 22.161 | 18.2189
2000 | [Hz] | - | 28.8931 | 18.5423 | 11.0387 | 52.9311 | 30.8739 | 13.7352 | 8.7606
4000 | [Hz] | - | 18.6732 | 5.8836 | < BGL | 41.0803 | 21.0341 | 5.4411 | 0.93666
8000 | [Hz] | - | < BGL | < BGL | < BGL | < BGL | 3.2061 | < BGL | < BGL
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  |  | HORIZONTAL FLOW |  |  |  | VERTICAL FLOW
|  | Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-1 SLB-1 | SLS-2 SLB-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4
|  | Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
|  | condition 1 | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors out/out | deflectors out/out | deflectors out/out | deflectors out/out
|  | condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
|  | condition 3 | SP--1 | SP--2 | SP--3 | SP--4 | SP--1 | SP--2 | SP--3 | SP--4
THROW
|  | Ak [m²] | 0.015233 | 0.024545 | 0.033858 | 0.04317 | 0.017819 | 0.022521 | 0.027223 | 0.031925
|  | K1 [m] | 2.9898 | 3.1928 | 3.3958 | 3.5987 | 5.5429 | 4.8125 | 4.082 | 3.3515
|  | X0 [m] | -0.76792 | -0.68901 | -0.6101 | -0.53119 | -5.543 | -4.5649 | -3.5867 | -2.6086
PRESSURE LOSS
|  | A | 39.8239 | 88.1777 | 118.3174 | 159.1897 | 55.4517 | 93.3568 | 131.2619 | 169.167
|  | B | 0.49896 | 0.50061 | 0.5061 | 0.49627 | 0.54942 | 0.54942 | 0.54942 | 0.54942
|  | Aduct [m²] | 0.012272 | 0.020106 | 0.031416 | 0.031416 | 0.012272 | 0.020106 | 0.031416 | 0.031416
CRITICAL DISTANCE (function of DT)
| at 4°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.1599 | -2.4874 | -2.6789 | -2.8148
| at 6°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.2672 | -2.5946 | -2.7862 | -2.9221
| at 8°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.3433 | -2.6707 | -2.8623 | -2.9982
| at 10°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.4023 | -2.7298 | -2.9213 | -3.0572
| at 12°C | A | 1.387 | 1.387 | 1.387 | 1.387
|  | B | -2.4505 | -2.778 | -2.9695 | -3.1054
TEMPERATURE
|  | Ak [m²] | 0.01403 | 0.02181 | 0.02959 | 0.03737
|  | K2 [-] | 1.1368 | 1.517 | 1.8973 | 2.2775
|  | X0 [m] | -0.099822 | -0.10102 | -0.10222 | -0.10341
SOUND POWER, NR
|  | A | 31.5349 | 30.2937 | 31.7033 | 32.6709 | 34.3684 | 34.0536 | 33.7984 | 33.9549
|  | B | -124.6955 | -142.6781 | -156.725 | -168.2022 | -151.5593 | -167.6681 | -179.9843 | -184.6509
SOUND POWER, dB(A)
|  | A | 28.8317 | 29.7404 | 28.8954 | 31.031 | 32.5585 | 31.3428 | 30.3266 | 30.3333
|  | B | -107.4515 | -134.2798 | -135.2064 | -154.037 | -137.9521 | -147.8471 | -154.3312 | -157.653
SOUND POWER SPECTRUM
| at 125 Hz | A | 22.5623 | 21.1999 | 22.3969 | 25.4369 | 21.2989 | 21.3206 | 21.2216 | 21.4546
|  | B | -70.3371 | -78.1363 | -86.9812 | -111.3244 | -84.0216 | -93.6086 | -100.7485 | -103.8922
| at 250 Hz | A | 25.9845 | 28.1731 | 29.484 | 30.3839 | 23.5042 | 23.5337 | 23.4186 | 23.6891
|  | B | -90.1659 | -120.6906 | -133.7542 | -144.428 | -91.6431 | -102.3543 | -110.2534 | -113.8521
| at 500 Hz | A | 30.715 | 32.8446 | 32.0228 | 33.6826 | 27.1037 | 27.1376 | 27.0049 | 27.3168
|  | B | -116.6534 | -154.6788 | -157.9978 | -174.7532 | -110.9466 | -125.9949 | -136.6812 | -141.9503
| at 1 kHz | A | 37.8021 | 38.8025 | 38.3526 | 41.3305 | 34.9936 | 35.0374 | 34.8661 | 35.2688
|  | B | -162.6972 | -194.6662 | -200.8858 | -226.862 | -155.2238 | -173.5725 | -186.7379 | -193.0926
| at 2 kHz | A | 43.2873 | 47.3986 | 46.488 | 44.8024 | 41.0381 | 41.0895 | 40.8886 | 41.3608
|  | B | -199.6188 | -255.0938 | -259.9889 | -257.3935 | -192.9473 | -215.3124 | -231.2472 | -239.0511
| at 4 kHz | A | 46.4959 | 44.7859 | 54.4997 | 70.436 | 37.4589 | 37.5058 | 37.3224 | 37.7534
|  | B | -225.9494 | -249.6598 | -320.6496 | -430.4359 | -183.3531 | -203.6804 | -218.1744 | -225.2614
| at 8 kHz | A | [5 empty] | 34.2415 | 34.075 | 34.4504
|  | B | [5 empty] | -201.9507 | -211.3383 | -214.9566
END

## IntermediateCalcul (hidden)
Critical distance
Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4 | SLS-1 SLB-1 | SLS-2 SLB-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4
Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
condition 1 | deflectors in/out | deflectors in/out | deflectors in/out | deflectors in/out | deflectors out/out | deflectors out/out | deflectors out/out | deflectors out/out
condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open) | 100% (open)
condition 3 | SP--1 | SP--2 | SP--3 | SP--4 | SP--1 | SP--2 | SP--3 | SP--4
A
dT
4 | 1.387 | 1.387 | 1.387 | 1.387
6 | 1.387 | 1.387 | 1.387 | 1.387
8 | 1.387 | 1.387 | 1.387 | 1.387
10 | 1.387 | 1.387 | 1.387 | 1.387
12 | 1.387 | 1.387 | 1.387 | 1.387
B
4 | -2.1599 | -2.4874 | -2.6789 | -2.8148
6 | -2.2672 | -2.5946 | -2.7862 | -2.9221
8 | -2.3433 | -2.6707 | -2.8623 | -2.9982
10 | -2.4023 | -2.7298 | -2.9213 | -3.0572
12 | -2.4505 | -2.778 | -2.9695 | -3.1054
dT requested
8
dT1 | 8 | 8 | 8 | 8
dT2 | 10 | 10 | 10 | 10
A1 | 1.387 | 1.387 | 1.387 | 1.387
A2 | 1.387 | 1.387 | 1.387 | 1.387
B1 | -2.3433 | -2.6707 | -2.8623 | -2.9982
B2 | -2.4023 | -2.7298 | -2.9213 | -3.0572

## CorrectionFactors (hidden)
Noise correction - diffuser length
cNR | -3.0985e-05
Throw correction - diffuser length
cK1 | 1