## SelectionData
Selection Table SLS / SLB / SLF
flow rate, Q | [m³/h] | 300
diffuser length, L | [mm] | 2000
room attenuation | [dB(A)] | 8
acoustics unit |  | dB(A)
| Type | SLS-1 SLB-1 | SLS-2 SLB-2 SLF-2 | SLS-3 SLB-3 SLF-3 | SLS-4 SLB-4 SLF-4
| L [mm] | 2000 | 2000 | 2000 | 2000
Airflow direction
| Damper position | 100% (open) | 100% (open) | 100% (open) | 100% (open)
| Plenum | SP--1 | SP--2 | SP--3 | SP--4
static pressure, DPs | [Pa] | 24.6286 | 7.3827 | 2.6192 | 2.3052
total pressure, DPtot | [Pa] | 26.3578 | 8.0269 | 2.883 | 2.5691
sound power, Lw | [dB(A)] | 34.7144 | <20 | <20 | <20
sound pressure, Lp | [dB(A)] | 26.7144 | <20 | <20 | <20
Sound Spectrum
Lw [dB]
125 | [Hz] | 26.2466 | - | - | -
250 | [Hz] | 26.5574 | - | - | -
500 | [Hz] | 28.4224 | - | - | -
1000 | [Hz] | 25.3769 | - | - | -
2000 | [Hz] | 20.5845 | - | - | -
4000 | [Hz] | 11.9293 | - | - | -
8000 | [Hz] | 3.6766 | - | - | -
< BGL : Lw below background level

## units (hidden)
dB(A)
NR

## TechData (hidden)
|  | Type | SL--1 | SL--2 | SL--3 | SL--4 | SL--1 | SL--2 | SL--3 | SL--4
|  | Size | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
|  | condition 1 | deflectors out/out | deflectors out/out | deflectors out/out | deflectors out/out | no deflectors | no deflectors | no deflectors | no deflectors
|  | condition 2 | 100% (open) | 100% (open) | 100% (open) | 100% (open) | SP--1 | SP--2 | SP--3 | SP--4
|  | condition 3 | SP--1 | SP--2 | SP--3 | SP--4
THROW
Ak [m²]
K1 [m]
X0 [m]
PRESSURE LOSS
|  | A | 32.7192 | 54.6391 | 93.4734 | 99.2269 | 39.1645 | 63.0377 | 100.0966 | 100.0966
|  | B | 0.47525 | 0.50516 | 0.4912 | 0.49477 | 0.46844 | 0.49523 | 0.49983 | 0.49983
|  | Aduct [m²] | 0.012272 | 0.020106 | 0.031416 | 0.031416 | 0.012272 | 0.020106 | 0.031416 | 0.031416
CRITICAL DISTANCE (function of DT)
| at 4°C | A
B
| at 6°C | A |  |  |  | -
B
| at 8°C | A
B
| at 10°C | A
B
| at 12°C | A
B
TEMPERATURE
Ak [m²]
K2 [-]
X0 [m]
SOUND POWER, NR
|  | A | 32.5052 | 29.337 | 29.5832 | 28.177 | 30.9154 | 26.7952 | 26.4821 | 26.4821
|  | B | -138.0352 | -141.3181 | -154.619 | -149.4835 | -136.8616 | -127.8142 | -137.1225 | -137.1225
SOUND POWER, dB(A)
|  | A | 29.0621 | 28.6477 | 27.7021 | 28.2002 | 30.0937 | 26.9186 | 25.2248 | 25.2248
|  | B | -114.5818 | -130.9566 | -137.2959 | -144.4382 | -126.7075 | -122.4451 | -123.9347 | -123.9347
SOUND POWER SPECTRUM
| at 125 Hz | A | 24.5823 | 23.4053 | 25.5464 | 23.0402 | 26.5537 | 22.8782 | 22.8153 | 22.8153
|  | B | -100.603 | -90.2109 | -131.2729 | -102.0688 | -100.5036 | -86.7882 | -97.1392 | -97.1392
| at 250 Hz | A | 29.2263 | 27.2834 | 30.016 | 26.11 | 28.7514 | 26.8516 | 24.6283 | 24.6283
|  | B | -123.5615 | -119.4258 | -157.3674 | -126.4447 | -115.2813 | -118.7339 | -115.5239 | -115.5239
| at 500 Hz | A | 32.8557 | 30.2554 | 32.2925 | 30.7979 | 30.7142 | 31.0725 | 28.2967 | 28.2967
|  | B | -139.8821 | -144.8715 | -175.3384 | -166.7273 | -133.0976 | -153.3405 | -149.6694 | -149.6694
| at 1 kHz | A | 35.1786 | 33.9068 | 35.8807 | 34.8533 | 32.1348 | 32.4829 | 31.8681 | 31.8681
|  | B | -154.5667 | -169.7726 | -198.7793 | -196.4041 | -144.7539 | -164.5543 | -177.2974 | -177.2974
| at 2 kHz | A | 43.0366 | 44.184 | 42.0951 | 44.4858 | 35.6204 | 38.7358 | 36.7019 | 36.7019
|  | B | -198.7328 | -236.2024 | -239.4812 | -261.96 | -170.3767 | -206.7933 | -213.7165 | -213.7165
| at 4 kHz | A | 51.3203 | 49.6902 | 47.1391 | 50.3976 | 45.1881 | 53.1708 | 45.3239 | 45.3239
|  | B | -248.8945 | -276.0121 | -277.2209 | -307.0789 | -229.6606 | -301.1652 | -275.6163 | -275.6163
| at 8 kHz | A |  | 45.3741 |  | 44.9128 | 49.4557 | 46.4826 | 48.6109 | 48.6109
|  | B |  | -259.7454 |  | -280.0736 | -260.8597 | -268.8856 | -304.8161 | -304.8161
END
[9 empty] | average of 3 and 4 slots | average of 3 and 4 slots

## CorrectionFactors (hidden)
Noise correction - diffuser length
cNR | 3.6766